## Sheet1
Point Name | Min | Default | Max | Units | Index | Class | Deadband | Quality Code | MM2 Support | MM3 Support | Notes
Analog Inputs (signed 32-bit integer)
Dnp3MapVersion | --- | 2.10.1 | --- | BCD | 0 | 0 | N/A | N | Y | Y | DRAFT - Derived from v2.10.0
TotalUpTime | 0 | 0 | 4294967295 | seconds | 1 | 0 | N/A | N | Y | Y
TotalPowerLowTime | 0 | 0 | 4294967295 | seconds | 2 | 0 | N/A | N | Y | Deprecated
ActiveUpTime | 0 | 0 | 4294967295 | seconds | 3 | 0 | N/A | N | Y | Y
ActivePowerLowTime | 0 | 0 | 4294967295 | seconds | 4 | 0 | N/A | N | Y | Deprecated
CndTemp | -40 | -1 | 365 | F | 5 | 1 | 2147483648 | Y | Y | Y
CndIrms | 0 | -1 | 10000 | A | 6 | 1 | 2147483648 | N | Y | Y
CndTempExcept | -40 | 0 | 365 | F | 7 | 1 | 0 | N | Y | Y | Resting value of 0, reports max values during event
CndIrmsExcept | 0 | 0 | 10000 | A | 8 | 1 | 0 | N | Y | Deprecated | Resting value of 0, reports max values during event
FciThreshFaultCurrent | 0 | 0 | 10000 | A | 9 | 1 | 0 | N | Y | Y | Licensed feature #1 Resting value of 0, reports max values during event
FciPercentFaultCurrent | 0 | 0 | 10000 | A | 10 | 1 | 0 | N | Y | Y | Licensed feature #1 Resting value of 0, reports max values during event
FciDiDtFaultCurrent | 0 | 0 | 10000 | A | 11 | 1 | 0 | N | Y | Y | Licensed feature #1 Resting value of 0, reports max values during event
YesterdayMaxIrms | 0 | 0 | 10000 | A | 12 | 0 | N/A | N | Y | Y | Maximum 5-minute average of Irms for the previous day. Changed to class 0 per CKSW-321.
YesterdayMaxTemp | -40 | 0 | 365 | F | 13 | 0 | N/A | N | Y | Y | Maximum 5-minute average of temperature for the previous day. Changed to class 0 per CKSW-321.
AvailableLogData | -2147483647 | 0 | 2147483648 | --- | 14 | 3 | 0 | N | Y | Y | SENTIENT USE ONLY. Code indicating the available data awaiting retrieval
LastCommandStatus | -2147483647 | 0 | 2147483648 | --- | 15 | 3 | 0 | N | Y | Y | SENTIENT USE ONLY. Code indicating the status of the last command
EIRelativePhaseDisplacement | -180 | 0 | 180 | degs | 16 | 1 | 2147483648 | N | N | Y | Phase difference between E-Field and Current
LatitudeInteger | -90 | 0 | 90 | fraction degs | 17 | 0 | N/A | Y | N | Y | Integer part of the latitude value.
LatitudeFraction1 | 0 | 0 | 9999 | fraction degs | 18 | 0 | N/A | Y | N | Y | Decimal part 1 of the latitude value.
LatitudeFraction2 | 0 | 0 | 9999 | fraction degs | 19 |  | N/A | Y | N | Y | Fraction part 1 of the latitude value.
LongitudeInteger | -180 | 0 | 180 | degs | 20 | 0 | N/A | Y | N | Y | Integer part of the logitude value.
LongitudeFraction1 | 0 | 0 | 9999 | fraction degs | 21 | 0 | N/A | Y | N | Y | Fraction part 1 of the logitude value.
LongitudeFraction2 | 0 | 0 | 9999 | fraction degs | 22 | 0 | N/A | Y | N | Y | Fraction part 2 of the logitude value.
Altitude | -10911 | 0 | 8850 | meters (ASL) | 23 | 0 | N/A | Y | N | Y
EnergyReserveVoltage | 0 | 0 | 5000 | millivolts | 24 | 0 | N/A | N | Reserved | Y | SENTIENT USE ONLY
TotalWanOffTime | 0 | 0 | 4294967295 | seconds | 25 | 0 | N/A | N | Reserved | Y
ActiveWanOffTime | 0 | 0 | 4294967295 | seconds | 26 | 0 | N/A | N | Reserved | Y
SoftwareVersion | --- | --- | --- | BCD | 27 | 0 | N/A | N | Y | Y | The software version of the device
OtapStatus | 0 | 0 | 300 | --- | 28 | 0 | N/A | N | N | Y | SENTIENT USE ONLY
DeviceType | --- | --- | --- | --- | 29 | 0 | N/A | N | Reserved | Y | 0 - Unknown type, 2 - MM3 SSN, 3 - MM3 LG, 4 - MM3 Sierra 5728v (3G cellular), 5 - MM3 Sierra MC7354(LTE), 6 - MM3 Telit Le910-NAG(LTE)
DeviceSerialNumber1 | --- | --- | --- | --- | 30 | 0 | N/A | N | Reserved | Y | ASCII codes of the alpha characters part of the serial number
DeviceSerialNumber2 | --- | --- | --- | --- | 31 | 0 | N/A | N | Reserved | Y | Numeric portion of serial number
LogIIrmsAlert1 | 0 | 0 | 1000 | A | 32 | 2 | N/A | N | Reserved | Y
LogIIrmsAlert2 | 0 | 0 | 1000 | A | 33 | 2 | N/A | N | Reserved | Y
LogITemperatureAlert1 | -40 | 0 | 300 | F | 34 | 2 | N/A | N | Reserved | Y
LogITemperatureAlert2 | -40 | 0 | 300 | F | 35 | 2 | N/A | N | Reserved | Y
FciPercentAutoThreshold | 50 | --- | 10000 | A | 36 | 0 | N/A | N | Reserved | Y
LocationAccuracyEstimate | 0 | 1001 | 1000 | meters (ASL) | 37 | 0 | N/A | Y | N | Y | Location accuracy measured in meters. Max of accuracy between latitude and longitude.
LocationFix | 0 | 1 | 3 |  | 38 | 0 | N/A | Y | N | Y | 0 – Unknown Fix, 1 – No Fix, 2 – 2D Fix, 3 – 3D Fix
AltitudeAccuracyEstimate | 0 | 1001 | 1000 | meters (ASL) | 39 | 0 | N/A | Y | N | Y | Altitude accuracy measured in meters
PhaseIdSignature | 0 | 0 | 4294967295 | --- | 40 | 0 | N/A | N | N | Y | Periodic measurements to support conductor phase ID
Binary Inputs
FieldMaintenanceAlert | 0 | 0 | 1 | boolean | 0 | 0 | N/A | N | Y | Deprecated | Changed from 1 to 0 as per ESW-121
PowerLowAlert | 0 | 0 | 1 | boolean | 1 | 0 | N/A | N | Y | Deprecated
BatteryMaintenanceAlert | 0 | 0 | 1 | boolean | 2 | 0 | N/A | N | Y | Reserved | 0 if battery condition is OK, 1 if not
FciLicenseEnabled | 0 | 0 | 1 | boolean | 3 | 0 | N/A | N | Y | Y | 1 if cFCI license enabled, 0 if not
FciFaultIndicationAlert | 0 | 0 | 1 | boolean | 4 | 1 | N/A | N | Y | Y | 1 if a FCI fault has been detected, 0 if not
FciLossOfSourceInProgress | 0 | 0 | 1 | boolean | 5 | 1 | N/A | N | Reserved | Y | 1 if Loss of Source is in progress
FciLedState | 0 | 0 | 1 | boolean | 6 | 3 | N/A | N | N | Y | 1 if FCI LED is on.
EfieldNotPresentAlert | 0 | 0 | 1 | boolean | 7 | 1 | N/A | N | N | Y
CurrentDirectionReversed | 0 | 0 | 1 | boolean | 8 | 1 | N/A | N | N | Y | The current E-I orientation. 0 implies Screw-to-LED on the Monitoring unit.
WanOffAlert | 0 | 0 | 1 | boolean | 9 | 1 | N/A | N | Reserved | Y
Counter Inputs (unsigned 32-bit integer)
SystemBootCounter | 0 | 0 | 4294967295 | --- | 0 | 0 | N/A | N | Y | Y
FieldMaintenanceAlertCounter | 0 | 0 | 4294967295 | --- | 1 | 0 | N/A | N | Y | Deprecated
PowerLowAlertCounter | 0 | 0 | 4294967295 | --- | 2 | 0 | N/A | N | Y | Deprecated
CndTempExceptCounter | 0 | 0 | 4294967295 | --- | 3 | 0 | N/A | N | Y | Y
CndIrmsExceptCounter | 0 | 0 | 4294967295 | --- | 4 | 0 | N/A | N | Y | Deprecated
FciThreshFaultCounter | 0 | 0 | 4294967295 | --- | 5 | 0 | N/A | N | Y | Y
FciPercentFaultCounter | 0 | 0 | 4294967295 | --- | 6 | 0 | N/A | N | Y | Y
FciDiDtFaultCounter | 0 | 0 | 4294967295 | --- | 7 | 0 | N/A | N | Y | Y
CaptureCounter | 0 | 0 | 4294967295 | -- | 8 | 0 | N/A | N | Reserved | Y
FciLossOfSourceCounter | 0 | 0 | 4294967295 | --- | 9 | 0 | N/A | N | Reserved | Y
EfieldNotPresentAlertCounter | 0 | 0 | 4294967295 | --- | 10 | 0 | N/A | N | N | Y | Count of number of times VoltageNotPresentAlert goes to 1
CurrentDirectionReversalCounter | 0 | 0 | 4294967295 | --- | 11 | 0 | N/A | N | N | Y | Count of number of times CurrentDirectionReversed changes value
WanOffCounter | 0 | 0 | 4294967295 | --- | 12 | 0 | N/A | N | Reserved | Y
DebugCounter | 0 | 0 | 4294967295 | --- | 13 | 0 | N/A | N | Y | Reserved | SENTIENT USE ONLY
AnomalyCounter | 0 | 0 | 4294967295 | --- | 14 | 0 | N/A | N | N | Y
DistClass1Counter | 0 | 0 | 4294967295 | --- | 15 | 0 | N/A | N | N | Y | Total number of Class1 disturbances detected. Class1 disturbances include, but is not limited to, faults.
DistClass2Counter | 0 | 0 | 4294967295 | --- | 16 | 0 | N/A | N | N | Y | Total number of Class2 disturbances detected. Class2 disturbances include, but is not limited to, load changes.
DistClass3Counter | 0 | 0 | 4294967295 | --- | 17 | 0 | N/A | N | N | Y | Total number of Class3 disturbances detected. Class3 disturbances include, but is not limited to, anomalies.
DistClass4Counter | 0 | 0 | 4294967295 | --- | 18 | 0 | N/A | N | N | Y | Total number of Class4 disturbances detected. Class4 disturbances include all disturbances not otherwise classified.
DistCapBankCounter | 0 | 0 | 4294967295 | --- | 19 | 0 | N/A | N | N | Y | Number of Capacitor Bank switching disturbances detected. Capacitor Bank switching disturbances are a Class2 disturbance.
Analog Outputs (signed 32-bit integer)
CndTempThresh | 0 | 185 | 300 | F | 0 | --- | N/A | N | Y | Y
CndIrmsThresh | 0 | 2000 | 10000 | A | 1 | --- | N/A | N | Y | Deprecated
EnableLicensedFeature | --- | 0 | --- | hash key | 2 | --- | N/A | N | Y | Deprecated | 256-bit hash based on feature id and unit serial number
FciThreshLimit | 20 | 2000 | 10000 | A | 3 | --- | N/A | N | Y | Y | Licensed feature #1
FciThreshMinDuration | 8 | 24 | 167 | msec | 4 | --- | N/A | N | Y | Y | Licensed feature #1
FciPercentLimit | 100 | 130 | 200 | % | 5 | --- | N/A | N | Y | Y | Licensed feature #1
FciPercentMinLimit | 50 | 50 | 200 | A | 6 | --- | N/A | N | Y | Y | Licensed feature #1
FciPercentSamplePeriod | 24 | 72 | 96 | hours | 7 | --- | N/A | N | Y | Y | Licensed feature #1
FciPercentMinDuration | 8 | 24 | 167 | msec | 8 | --- | N/A | N | Y | Y | Licensed feature #1
FciDiDtLimit | 10 | 100 | 500 | A | 9 | --- | N/A | N | Y | Y | Licensed feature #1
FciDiDtRiseTime | 8 | 24 | 167 | msec | 10 | --- | N/A | N | Y | Y | Licensed feature #1
FciInrushDelay | 0 | 120000 | 120000 | msec | 11 | --- | N/A | N | Y | Y | Licensed feature #1 Duration where inrush current will be squelched
FciLedTimeoutDuration | 10 | 10800 | 32400 | seconds | 12 | --- | N/A | N | Y | Y | Licensed feature #1 Maximum duration that the FCI LED will blink
FciNormalLimit | 10 | 10 | 1000 | A | 13 | --- | N/A | N | Y | Y | Licensed feature #1 IRMS threshold under which is "normal" operation
FciNormalMinDuration | 0 | 60 | 600 | seconds | 14 | --- | N/A | N | Y | Y | Licensed feature #1 Duration required for FciNormalLimit
FciTemporaryMaxDuration | 60 | 0 | 600 | seconds | 15 | --- | N/A | N | Deprecated | Deprecated
GenerateLogPackage | -2147483647 | 0 | 2147483648 | --- | 16 | --- | N/A | N | Y | Y | Code indicating the data that should be included in the generated package
LocalTimeOffset | --- | 0 | --- | --- | 17 | --- | N/A | N | Y | Y | The time offset to convert from DNP network time to local time.
FciDiDtMinDuration | 24 | 24 | 167 | msec | 18 | --- | N/A | N | Reserved | Y | Licensed feature #1
FciLossOfSourceFallLimitPercent | 3 | 90 | 100 | % | 19 | --- | N/A | N | Reserved | Y | Licensed feature #1
FciLossOfSourceFallTime | 8 | 24 | 167 | msec | 20 | --- | N/A | N | Reserved | Y | Licensed feature #1
FciLossOfSourceMinDuration | 8 | 24 | 167 | msec | 21 | --- | N/A | N | Reserved | Y | Licensed feature #1
FciLossOfSourceFinalLevel | 0 | 3 | 100 | A | 22 | --- | N/A | N | Reserved | Y | Licensed feature #1
FciPreInrushLowCurrentMinDuration | 8 | 100 | 6000 | msec | 23 | --- | N/A | N | Y | Y | Licensed feature #1
LogIIrmsThreshold1 | 0 | 600 | 1000 | A | 24 | --- | N/A | N | Reserved | Y | Associates with LogIIrmsAlert1
LogIIrmsThreshold2 | 0 | 300 | 1000 | A | 25 | --- | N/A | N | Reserved | Y | Associates with LogIIrmsAlert2
LogITemperatureThreshold1 | -40 | 176 | 300 | F | 26 | --- | N/A | N | Reserved | Y | Associates with LogITemperatureAlert1
LogITemperatureThreshold2 | -40 | 104 | 300 | F | 27 | --- | N/A | N | Reserved | Y | Associates with LogITemperatureAlert2
AnomalyGuardBandSize | 0 | 32 | 130 | samples | 28 | --- | N/A | N | N | Y | Analysis guard time
AnomalyKsigToStart | 0 | 40 | 100 | tenths | 29 | --- | N/A | N | N | Y | Start capture trigger threshold
AnomalyCurrentNoiseFloor | 0 | 10 | 100 | tenths A | 30 | --- | N/A | N | N | Y | Minimum detectable level
AnomalyMinSnrToStop | 0 | 100 | 200 | tenths | 31 | --- | N/A | N | N | Y | Stop capture trigger threshold
AnomalyWindowSize | 2 | 651 | 1300 | samples | 32 | --- | N/A | N | N | Y | Capture window sample size
DnpUTCTimeOffset | -1200 | 0 | 1200 | --- | 33 | --- | N/A | N | N | Y | The time offset from UTC to local time. Format is =/-HHMM
DnpStaleStackTime | 0 | 604800 | 5184000 | seconds | 34 | --- | N/A | N | N | Y | The amount of time a stack has failed to receive a master request, is considered stale, and is deleted. A value of 0 disables stale stack detection/removal.
DnpDSTOn | 0 | 0 | 206968635 | --- | 35 | --- | N/A | N | N | Y | Determines when DST is enabled. Format is MWDHHMM where M is month, W is week of month, D is day of week, HH is hour and MM is minutes.
DnpDSTOff | 0 | 0 | 206968635 | --- | 36 | --- | N/A | N | N | Y | Determines when DST is disable. Format is MWDHHMM where M is month, W is week of month, D is day of week, HH is hour and MM is minutes.
DnpDSTTimeOffset | -1200 | 0 | 1200 | --- | 37 | --- | N/A | N | N | Y | The DST time adjustment. Format is +/- HHMM.
Binary Outputs
MasterRebootPulse | 0 | 0 | 1 | boolean | 0 | --- | N/A | N | Y | Y
FieldMaintenanceLatch | 0 | 1 | 1 | boolean | 1 | --- | N/A | N | Y | Deprecated
ReserveModeLatch | 0 | 1 | 1 | boolean | 2 | --- | N/A | N | Deprecated | Deprecated
IndLedLatch | 0 | 0 | 1 | boolean | 3 | --- | N/A | N | Y | Reserved
FciLedLatch | 0 | 0 | 1 | boolean | 4 | --- | N/A | N | Y | Y
FciMasterEnableLatch | 0 | 0 | 1 | boolean | 5 | --- | N/A | N | Y | Y | Licensed feature #1 Disables cFCI feature without changing other settings
FciLocalAnunciatorLatch | 0 | 0 | 1 | boolean | 6 | --- | N/A | N | Y | Y | Licensed feature #1 0 for remote operation, 1 for local operation
FciThreshEnabledLatch | 0 | 0 | 1 | boolean | 7 | --- | N/A | N | Y | Y | Licensed feature #1
FciPercentEnabledLatch | 0 | 0 | 1 | boolean | 8 | --- | N/A | N | Y | Y | Licensed feature #1
FciDiDtEnabledLatch | 0 | 0 | 1 | boolean | 9 | --- | N/A | N | Y | Y | Licensed feature #1
FciResetPulse | 0 | 0 | 1 | boolean | 10 | --- | N/A | N | Y | Y | Licensed feature #1 Allows operator to acknowledge/retire a fault early
FciLossOfSourceEnabledLatch | 0 | 0 | 1 | boolean | 11 | --- | N/A | N | Reserved | Y | Licensed feature #1
FciLedStateEnabledLatch | 0 | 0 | 1 | boolean | 12 | --- | N/A | N | Reserved | Y
CurrentDirectionInvert | 0 | 1 | 1 | boolean | 13 | --- | N/A | N | N | Y
EfieldNotPresentEnableLatch | 0 | 0 | 1 | boolean | 14 | --- | N/A | N | N | Y | Disables E-field not present detection
CurrentDirectionReversedEnableLatch | 0 | 0 | 1 | boolean | 15 | --- | N/A | N | N | Y | Disables current direction detection
GpsEnableLatch | 0 | 1 | 1 | boolean | 16 | --- | N/A | N | N | Y | Disables GPS
WanOffAlertEnableLatch | 0 | 1 | 1 | boolean | 17 | --- | N/A | N | Reserved | Y
OtapStart | 0 | 0 | 1 | boolean | 18 | --- | N/A | N | N | Y | SENTIENT USE ONLY
OtapStatusClear | 0 | 0 | 1 | boolean | 19 | --- | N/A | N | N | Y | SENTIENT USE ONLY
LogIAlertEnableLatch | 0 | 0 | 1 | boolean | 20 | --- | N/A | N | Reserved | Y
LogILoggingEnableLatch | 0 | 0 | 1 | boolean | 21 | --- | N/A | N | Reserved | Y
AnomalyEnableLatch | 0 | 0 | 1 | boolean | 22 | --- | N/A | N | N | Y
PhaseIdEnableLatch | 0 | 0 | 1 | boolean | 23 | --- | N/A | N | N | Y | Enable measurements to support conductor phase ID
DisturbanceClassificationEnableLatch | 0 | 1 | 1 | boolean | 24 | --- | N/A | N | N | Y | Enable waveform disturbance classification feature. This feature is enabled by default. The counters DistClass1Counter, DistClass2Counter, DistClass3Counter, and DistClass4Counter are updated as appropriate when this feature is enabled.